# Energy Scavenger Hunt Workbook

US DOE Better Plants Energy Bootcamp

Baseline data collection workbook for manufacturing facility energy opportunities

Use this workbook during a facility energy scavenger hunt to document current operating conditions for later entry into MEASUR calculators. Record measured values and their sources; do not enter proposed conditions or calculated savings.

| Workbook information | Entry |
| --- | --- |
| Document revision |  |
| Revision date |  |
| Facility |  |
| Area or department |  |

Default units: Imperial

Contents

Pump Systems	3

Opportunity 1 Shut off pumps when not needed	3

Opportunity 2 Use VFD control instead of throttling valves	5

Fan Systems	7

Opportunity 1 Shut off fans when not needed	7

Opportunity 2 Use VFD control instead of outlet dampers	9

Opportunity 3 Use a notched V-belt instead of a smooth V-belt	10

Lighting Systems	11

Opportunity 1 Turn off unnecessary light fixtures	11

Opportunity 2 Replace inefficient light fixtures with LED fixtures	13

Process Heating Systems	15

Opportunity 1 Optimize the air to fuel ratio	15

Opportunity 2 Improve furnace insulation to reduce wall loss	17

Opportunity 3 Recover waste heat from flue gas	19

Compressed Air Systems	21

Opportunity 1 Check the velocity in compressed air piping	21

Opportunity 2 Reduce inappropriate compressed air use	23

Opportunity 3 Quantify compressed air leaks using the bag method	25

Facility and assessment setup

| Setup field | Entry |
| --- | --- |
| Facility |  |
| Area or department |  |
| Assessment date |  |
| Lead assessor |  |
| Team members |  |
| Electricity rate | $/kWh |
| Natural gas or fuel rate | Cost and unit: |
| Purchased compressed air rate | Cost and unit: |
| Normal operating schedule |  |
| Data and source quality notes |  |

How to use this workbook

Complete the facility setup once, then use one opportunity record for each equipment item or group.

Capture the current baseline only. Do not estimate a proposed condition or savings in the field.

Use the source column to record the meter, nameplate, drawing, operator interview, or plant record used.

Mark assumptions clearly and take photographs of nameplates, controls, gauges, and measurement locations when permitted.

Duplicate opportunity records when several non-identical equipment items are observed.

Source quality key

| Source quality | Meaning |
| --- | --- |
| Measured | Direct field measurement taken during the assessment. |
| Nameplate | Equipment or component nameplate value. |
| Plant Record | Historian, utility bill, drawing, work order, or other facility record. |
| Estimated | Engineering estimate or rule-of-thumb; document the basis. |
| Unknown | Required value was not available and needs follow-up. |

# Pump Systems

Use these records to document pumps that operate unnecessarily and throttled pumping systems that may be candidates for variable-speed control.

## Opportunity 1 Shut off pumps when not needed

| MEASUR path: General > Electricity Reduction https://measur.ornl.gov/calculators/electricity-reduction | Scan to open |
| --- | --- |

Calculator context. Electricity Reduction quantifies changes in electricity use caused by reducing operating time or turning off equipment. This record captures the present operating schedule and electrical demand only.

### Record identification

| Record field | Entry |
| --- | --- |
| Pump or equipment tag |  |
| Area or process served |  |
| Assessment record number |  |

### Baseline inputs for Electricity Reduction

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Equipment or pump tag | Facility name or tag for the operating equipment. |  |  |
| Annual operating hours | Number of hours the equipment is on annually, including normally scheduled overtime. | hrs/yr |  |
| Electricity cost | Facility electricity cost per kilowatt-hour. | $/kWh |  |
| Measurement method | Primary field path for this record. |  | Multimeter Reading |
| Number of phases | Select 1 for single-phase or 3 for three-phase equipment. | 1 or 3 |  |
| Supply voltage | Voltage measured while the equipment is operating. | V |  |
| Average current | Average current measured in the observed baseline condition. | A |  |
| Power factor | Use the plant uncorrected power factor when available. |  |  |
| Number of identical units | Number of identical units represented by this record; use 1 if they differ. | count |  |

### Optional alternate measurement data

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Power meter reading | Use when a measured real-power value is available. | kW |  |
| Nameplate motor power | Use for a nameplate-based estimate. | hp |  |
| Motor and drive efficiency | Combined ratio of mechanical output to electrical input. | % |  |
| Percent loaded | Estimated load compared with nameplate rating. | % |  |
| Existing annual energy | Use only when annual energy is available from another documented source. | kWh |  |

### Field notes

| Document these observations | Notes |
| --- | --- |
| Schedule evidence; Controls or interlocks; Observed idle operation; Photographs, meter IDs, and source notes. |  |

### Ready for MEASUR entry

|  | Baseline check |  | Baseline check |
| --- | --- | --- | --- |
| [ ] | Operating hours and electricity rate are documented. | [ ] | Multimeter fields are complete or an alternate measurement method is identified. |
| [ ] | The number of identical pumps is confirmed. | [ ] | Only the current operating condition is recorded. |

## Opportunity 2 Use VFD control instead of throttling valves

| MEASUR path: Pumps > Valve Energy Loss https://measur.ornl.gov/calculators/valve-energy-loss | Scan to open |
| --- | --- |

Calculator context. A throttled valve dissipates fluid power to control flow. Valve Energy Loss estimates the present energy associated with the measured flow and pressure conditions across the valve.

### Record identification

| Record field | Entry |
| --- | --- |
| Pump and valve tag |  |
| System or process served |  |
| Assessment record number |  |

### Baseline inputs for Valve Energy Loss

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Annual operating hours | Hours the valve participates in the pumping system each year. | hrs/yr |  |
| Electricity cost | Facility electricity cost per kilowatt-hour. | $/kWh |  |
| Pump efficiency | Use documented efficiency; 85% may be used as a marked estimate if unknown. | % |  |
| Motor efficiency | Nameplate value is preferred; 95% may be used as a marked estimate if unknown. | % |  |
| Fluid specific gravity | Density relative to water; water equals 1. |  |  |
| Flow rate | Volume flow through the valve in the observed throttled condition. | gpm |  |
| Upstream pressure | Gauge pressure immediately before the valve. | psi |  |
| Upstream gauge elevation | Gauge elevation relative to the valve; may be negative, zero, or positive. | ft |  |
| Downstream pressure | Gauge pressure immediately after the valve. | psi |  |
| Downstream gauge elevation | Gauge elevation relative to the valve; may be negative, zero, or positive. | ft |  |

### Field notes

| Document these observations | Notes |
| --- | --- |
| Valve position and throttling behavior; Flow and pressure measurement locations; Whether a VFD exists today; Gauge IDs, photographs, and source notes. |  |

### Ready for MEASUR entry

|  | Baseline check |  | Baseline check |
| --- | --- | --- | --- |
| [ ] | Flow and pressure readings represent the same current operating condition. | [ ] | Pump and motor efficiencies are documented or estimates are marked. |
| [ ] | Gauge elevations are recorded relative to the valve. | [ ] | Pipe diameters and valve diameter are not required by the current calculation. |

# Fan Systems

Use these records to document unnecessary fan operation, damper-controlled systems, and belt-drive conditions.

## Opportunity 1 Shut off fans when not needed

| MEASUR path: General > Electricity Reduction https://measur.ornl.gov/calculators/electricity-reduction | Scan to open |
| --- | --- |

Calculator context. Electricity Reduction supports opportunities that reduce fan operating time or turn off fans during periods when airflow is not required.

### Record identification

| Record field | Entry |
| --- | --- |
| Fan or motor tag |  |
| Area or process served |  |
| Assessment record number |  |

### Baseline inputs for Electricity Reduction

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Fan or motor tag | Facility name or tag for the operating equipment. |  |  |
| Annual operating hours | Number of hours the equipment is on annually, including normally scheduled overtime. | hrs/yr |  |
| Electricity cost | Facility electricity cost per kilowatt-hour. | $/kWh |  |
| Measurement method | Primary field path for this record. |  | Multimeter Reading |
| Number of phases | Select 1 for single-phase or 3 for three-phase equipment. | 1 or 3 |  |
| Supply voltage | Voltage measured while the equipment is operating. | V |  |
| Average current | Average current measured in the observed baseline condition. | A |  |
| Power factor | Use the plant uncorrected power factor when available. |  |  |
| Number of identical units | Number of identical units represented by this record; use 1 if they differ. | count |  |

### Optional alternate measurement data

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Power meter reading | Use when a measured real-power value is available. | kW |  |
| Nameplate motor power | Use for a nameplate-based estimate. | hp |  |
| Motor and drive efficiency | Combined ratio of mechanical output to electrical input. | % |  |
| Percent loaded | Estimated load compared with nameplate rating. | % |  |
| Variable-speed motor | Record whether the motor operates on variable-frequency control. | Yes/No |  |
| Operating frequency | Observed drive output frequency in the current condition. | Hz |  |
| Line frequency | Nameplate or facility line frequency. | Hz |  |
| Existing annual energy | Use only when annual energy is available from another documented source. | kWh |  |

### Field notes

| Document these observations | Notes |
| --- | --- |
| Schedule evidence; Controls, interlocks, or occupancy signals; Observed idle operation; Photographs, meter IDs, and source notes. |  |

### Ready for MEASUR entry

|  | Baseline check |  | Baseline check |
| --- | --- | --- | --- |
| [ ] | Operating hours and electricity rate are documented. | [ ] | The active measurement method and its required fields are complete. |
| [ ] | The number of identical fans is confirmed. | [ ] | Only the current operating condition is recorded. |

## Opportunity 2 Use VFD control instead of outlet dampers

| MEASUR path: Field screening only | No direct calculator |
| --- | --- |

Calculator context. MEASUR does not currently provide a direct calculator for this opportunity. Record the current fan, airflow, speed, pressure, and control condition so the opportunity can be evaluated later.

### Record identification

| Record field | Entry |
| --- | --- |
| Fan or motor tag |  |
| Area or process served |  |
| Assessment record number |  |

### Current-condition screening inputs

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Annual operating hours | Current yearly operating time. | hrs/yr |  |
| Airflow | Measured or documented airflow in the current condition. | cfm |  |
| Current motor speed | Observed operating speed during the measurement. | rpm |  |
| Rated or full-load speed | Motor or fan nameplate speed. | rpm |  |
| Discharge static pressure | Pressure measured with the current damper position. | in. w.g. |  |
| Current control method | Damper, inlet guide vane, cycling, VFD, or other. |  |  |
| Damper position | Observed or control-system position under the measured load. | % open |  |
| VFD currently installed | Record whether variable-speed control already exists. | Yes/No |  |

### Field notes

| Document these observations | Notes |
| --- | --- |
| Airflow and pressure measurement locations; Production state during observation; Control sequence or operator practice; Photographs and source notes. |  |

### Ready for MEASUR entry

|  | Baseline check |  | Baseline check |
| --- | --- | --- | --- |
| [ ] | Airflow, speed, and static pressure represent the same current condition. | [ ] | The current control method and damper position are documented. |
| [ ] | No proposed speed or future pressure value is entered. | [ ] | The record is clearly marked as screening data rather than calculator-ready data. |

## Opportunity 3 Use a notched V-belt instead of a smooth V-belt

| MEASUR path: Motors > Motor Drive Comparison https://measur.ornl.gov/calculators/motor-drive | Scan to open |
| --- | --- |

Calculator context. Motor Drive Comparison compares the energy use of standard V-belts, notched belts, synchronous belts, and direct drives. Belt efficiency depends on alignment, tension, wear, loading, and pulley condition.

### Record identification

| Record field | Entry |
| --- | --- |
| Fan and motor tag |  |
| Driven equipment or process |  |
| Assessment record number |  |

### Baseline inputs for Motor Drive Comparison

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Annual operating hours | Number of hours the motor operates each year. | hrs/yr |  |
| Electricity cost | Facility electricity cost per kilowatt-hour. | $/kWh |  |
| Motor power | Motor nameplate power rating. | hp |  |
| Percent loaded | Average load relative to rated motor power; measured values are preferred. | % |  |
| Current drive type | Standard V-belt, notched V-belt, synchronous belt, or direct drive. |  |  |

### Field notes

| Document these observations | Notes |
| --- | --- |
| Belt type and quantity; Belt and pulley condition; Alignment and tension observations; Inspection method, photographs, and source notes. |  |

### Ready for MEASUR entry

|  | Baseline check |  | Baseline check |
| --- | --- | --- | --- |
| [ ] | Motor power, load, annual hours, and electricity cost are available. | [ ] | The current drive type is confirmed by inspection. |
| [ ] | Belt condition and maintenance observations are documented. | [ ] | No replacement drive type is required in this baseline workbook. |

# Lighting Systems

Use these records to document lighting that operates unnecessarily and the existing fixture information needed for a future lighting upgrade analysis.

## Opportunity 1 Turn off unnecessary light fixtures

| MEASUR path: General > Electricity Reduction https://measur.ornl.gov/calculators/electricity-reduction | Scan to open |
| --- | --- |

Calculator context. Electricity Reduction can document the present power and operating time of fixture groups that may be turned off or scheduled for fewer hours. A power-meter reading is the preferred field path.

### Record identification

| Record field | Entry |
| --- | --- |
| Fixture group or panel |  |
| Area served |  |
| Assessment record number |  |

### Primary power-meter baseline inputs

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Fixture group or area | Name the measured fixture group, panel, or circuit. |  |  |
| Annual operating hours | Hours per year the fixtures are energized, including overtime. | hrs/yr |  |
| Electricity cost | Facility electricity cost per kilowatt-hour. | $/kWh |  |
| Measurement method | Preferred field path for lighting circuits or groups. |  | Power Meter Reading |
| Measured power | Real power for one fixture or the identified group. | kW |  |
| Number of identical units | Number of identical fixtures or groups represented by the measured power. | count |  |

### Optional multimeter or existing-energy data

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Number of phases | Select 1 or 3 for the measured circuit. | 1 or 3 |  |
| Supply voltage | Measured circuit voltage. | V |  |
| Average current | Measured operating current. | A |  |
| Power factor | Use the measured or documented uncorrected value. |  |  |
| Existing annual energy | Annual lighting energy from a documented meter, submeter, or study. | kWh |  |

### Field notes

| Document these observations | Notes |
| --- | --- |
| Lighting schedule evidence; Occupancy or daylight controls; Observed unoccupied or daylight periods; Meter, panel, photographs, and source notes. |  |

### Ready for MEASUR entry

|  | Baseline check |  | Baseline check |
| --- | --- | --- | --- |
| [ ] | The fixture group and annual operating hours are documented. | [ ] | Power-meter data are complete or the alternate data source is identified. |
| [ ] | The number of identical fixtures or groups is confirmed. | [ ] | Only the current energized condition is recorded. |

## Opportunity 2 Replace inefficient light fixtures with LED fixtures

| MEASUR path: Lighting > Lighting Replacement https://measur.ornl.gov/calculators/lighting-replacement | Scan to open |
| --- | --- |

Calculator context. Lighting Replacement evaluates fixture power, quantity, operating time, and optional lighting-level characteristics. This record documents only the existing fixtures.

### Record identification

| Record field | Entry |
| --- | --- |
| Fixture group name |  |
| Area or task served |  |
| Assessment record number |  |

### Existing fixture baseline inputs

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Operating hours | Hours per year the lighting is on; this may differ from facility operating time. | hrs/yr |  |
| Electricity cost | Facility electricity cost per kilowatt-hour. | $/kWh |  |
| Fixture category | Select the matching MEASUR fixture category. |  |  |
| Fixture type | Select the closest fixture subtype or document a custom fixture. |  |  |
| Watts per lamp | Power used by each lamp or bulb. | W/lamp |  |
| Ballast factor | Fraction representing ballast output; typical values are approximately 0.7 to 1.2. |  |  |
| Lamps per fixture | Number of lamps or bulbs in each fixture. | count |  |
| Number of fixtures | Total number of identical existing fixtures. | count |  |

### Optional lighting-level inputs

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Lumens per lamp | Rated light output for each lamp. | lm/lamp |  |
| Coefficient of utilization | Fraction of luminaire output reaching the work plane. |  |  |
| Lumen degradation factor | Ratio of maintained lumen output to initial output. |  |  |
| Lamp life | Documented rated life from the selected fixture data. | hrs |  |

### Field notes

| Document these observations | Notes |
| --- | --- |
| Fixture and ballast nameplate information; Existing controls and schedule; Lighting-level or task observations; Photographs and source notes. |  |

### Ready for MEASUR entry

|  | Baseline check |  | Baseline check |
| --- | --- | --- | --- |
| [ ] | Existing fixture type, lamp power, lamps per fixture, and fixture count are documented. | [ ] | Operating hours and electricity cost are available. |
| [ ] | Optional lighting-level fields are completed or marked unavailable. | [ ] | No replacement fixture is entered in this baseline workbook. |

# Process Heating Systems

Use these records to document current combustion exhaust conditions, furnace surface losses, and exhaust streams that may support waste heat recovery.

## Opportunity 1 Optimize the air to fuel ratio

| MEASUR path: Process Heating > Flue Gas Loss https://measur.ornl.gov/calculators/flue-gas | Scan to open |
| --- | --- |

Calculator context. Flue Gas Loss estimates available heat and exhaust losses from fuel properties, temperatures, and either measured oxygen or excess air. Use one consistent, steady operating condition.

### Record identification

| Record field | Entry |
| --- | --- |
| Furnace, oven, or burner tag |  |
| Process and operating state |  |
| Assessment record number |  |

### Baseline inputs for Flue Gas Loss

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Annual operating hours | Number of hours the heating equipment operates each year. | hrs/yr |  |
| Fuel cost | Cost per selected MEASUR energy unit. | $/unit |  |
| Fuel form | Select Gas by Volume or Solid/Liquid by Mass. |  | Gas by Volume |
| Fuel preset | Select the closest standard MEASUR fuel; use the custom table only if needed. |  |  |
| Flue gas temperature | Temperature at the documented exhaust measurement location. | deg F |  |
| Ambient air temperature | Temperature of the air surrounding the combustion equipment. | deg F |  |
| Oxygen calculation method | Record whether oxygen in flue gas or excess air is known. |  |  |
| O2 in flue gas | Dry flue-gas oxygen concentration when this method is used. | % |  |
| Excess air | Enter instead of O2 when excess air is the known value. | % |  |
| Combustion air temperature | Temperature of air supplied for combustion. | deg F |  |
| Fuel temperature | Temperature of fuel entering the combustion process. | deg F |  |
| Moisture in combustion air | Moisture content used by the MEASUR fuel calculation. | % |  |
| Fuel consumption | Current fuel heat input rate for the baseline condition. | MMBtu/hr |  |

### Additional solid or liquid fuel inputs

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Ash discharge temperature | Temperature of ash leaving the combustion process. | deg F |  |
| Unburned carbon in ash | Mass fraction of unburned carbon in discharged ash. | % |  |

### Optional custom fuel composition

Complete only when a standard MEASUR fuel preset is unavailable. Gas values are volume percent; solid or liquid values are mass percent.

| Custom gas | Value | Custom gas | Value | Custom solid/liquid | Value |
| --- | --- | --- | --- | --- | --- |
| Methane CH4 (%) |  | Ethane C2H6 (%) |  | Carbon (%) |  |
| Nitrogen N2 (%) |  | Hydrogen H2 (%) |  | Hydrogen (%) |  |
| Propane C3H8 (%) |  | Butane and higher (%) |  | Sulfur (%) |  |
| Water H2O (%) |  | Carbon monoxide CO (%) |  | Inert ash (%) |  |
| Carbon dioxide CO2 (%) |  | Sulfur dioxide SO2 (%) |  | Oxygen (%) |  |
| Oxygen O2 (%) |  | Higher heating value (Btu/scf) |  | Moisture (%) |  |
| Specific gravity |  |  |  | Nitrogen (%) |  |
|  |  |  |  | Higher heating value (Btu/lb) |  |

### Field notes

| Document these observations | Notes |
| --- | --- |
| Analyzer and calibration information; Flue gas measurement location; Burner load and production state; Photographs and source notes. |  |

### Ready for MEASUR entry

|  | Baseline check |  | Baseline check |
| --- | --- | --- | --- |
| [ ] | Fuel form and fuel preset or custom composition are documented. | [ ] | Temperatures and oxygen or excess-air data represent the same operating condition. |
| [ ] | Fuel consumption, annual hours, and fuel cost are available. | [ ] | Only the current combustion condition is recorded. |

## Opportunity 2 Improve furnace insulation to reduce wall loss

| MEASUR path: Process Heating > Wall Loss https://measur.ornl.gov/calculators/wall-loss | Scan to open |
| --- | --- |

Calculator context. Wall Loss estimates heat transferred from exposed equipment surfaces to the surroundings by convection and radiation. Use representative surface measurements and document the area they represent.

### Record identification

| Record field | Entry |
| --- | --- |
| Furnace or equipment tag |  |
| Surface or zone identifier |  |
| Assessment record number |  |

### Baseline inputs for Wall Loss

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Energy source type | Fuel, electricity, or purchased steam used by the equipment. |  |  |
| Annual operating hours | Number of hours the surface remains at the recorded condition each year. | hrs/yr |  |
| Energy or fuel cost | Cost per selected MEASUR energy unit. | $/unit |  |
| Available heat or efficiency | Available heat for fuel, boiler efficiency for steam, or system efficiency for electricity. | % |  |
| Average surface temperature | Weighted average of representative outside-surface measurements. | deg F |  |
| Ambient temperature | Representative surrounding air temperature. | deg F |  |
| Wind velocity | Average velocity over the surface; zero is often appropriate indoors if marked as an assumption. | mph |  |
| Surface shape and orientation | Select the closest MEASUR surface geometry and orientation. |  |  |
| Shape or orientation factor | Record the factor associated with the selected surface. |  |  |
| Surface emissivity | Use measured or documented emissivity; 0.9 may be a marked estimate for many dark or oxidized surfaces. | 0 to 1 |  |
| Total exposed surface area | Outside area represented by the temperature measurement. | ft2 |  |
| Correction factor | Engineering correction factor; use 1 when no correction is needed. |  | 1 |

### Field notes

| Document these observations | Notes |
| --- | --- |
| Temperature measurement grid and emissivity setting; Surface construction or insulation condition; Ambient and wind measurement location; Photographs and source notes. |  |

### Ready for MEASUR entry

|  | Baseline check |  | Baseline check |
| --- | --- | --- | --- |
| [ ] | Average surface temperature and represented area are documented. | [ ] | Energy source, annual hours, cost, and available heat or efficiency are available. |
| [ ] | Emissivity, wind, and correction-factor assumptions are marked. | [ ] | No post-insulation surface temperature is entered. |

## Opportunity 3 Recover waste heat from flue gas

| MEASUR path: Process Heating > Flue Gas Loss https://measur.ornl.gov/calculators/flue-gas | Scan to open |
| --- | --- |

Calculator context. Flue Gas Loss documents the energy carried by the current exhaust stream. Record the location relative to any existing recuperator, economizer, or other recovery equipment.

### Record identification

| Record field | Entry |
| --- | --- |
| Furnace, oven, or exhaust tag |  |
| Process and operating state |  |
| Assessment record number |  |

### Current exhaust baseline inputs

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Annual operating hours | Number of hours the heating equipment operates each year. | hrs/yr |  |
| Fuel cost | Cost per selected MEASUR energy unit. | $/unit |  |
| Fuel form | Select Gas by Volume or Solid/Liquid by Mass. |  | Gas by Volume |
| Fuel preset | Select the closest standard MEASUR fuel; use the custom table only if needed. |  |  |
| Flue gas temperature | Temperature at the documented exhaust measurement location. | deg F |  |
| Ambient air temperature | Temperature of the air surrounding the combustion equipment. | deg F |  |
| Oxygen calculation method | Record whether oxygen in flue gas or excess air is known. |  |  |
| O2 in flue gas | Dry flue-gas oxygen concentration when this method is used. | % |  |
| Excess air | Enter instead of O2 when excess air is the known value. | % |  |
| Combustion air temperature | Temperature of air supplied for combustion. | deg F |  |
| Fuel temperature | Temperature of fuel entering the combustion process. | deg F |  |
| Moisture in combustion air | Moisture content used by the MEASUR fuel calculation. | % |  |
| Fuel consumption | Current fuel heat input rate for the baseline condition. | MMBtu/hr |  |

### Additional solid or liquid fuel inputs

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Ash discharge temperature | Temperature of ash leaving the combustion process. | deg F |  |
| Unburned carbon in ash | Mass fraction of unburned carbon in discharged ash. | % |  |

### Optional custom fuel composition

Complete only when a standard MEASUR fuel preset is unavailable. Gas values are volume percent; solid or liquid values are mass percent.

| Custom gas | Value | Custom gas | Value | Custom solid/liquid | Value |
| --- | --- | --- | --- | --- | --- |
| Methane CH4 (%) |  | Ethane C2H6 (%) |  | Carbon (%) |  |
| Nitrogen N2 (%) |  | Hydrogen H2 (%) |  | Hydrogen (%) |  |
| Propane C3H8 (%) |  | Butane and higher (%) |  | Sulfur (%) |  |
| Water H2O (%) |  | Carbon monoxide CO (%) |  | Inert ash (%) |  |
| Carbon dioxide CO2 (%) |  | Sulfur dioxide SO2 (%) |  | Oxygen (%) |  |
| Oxygen O2 (%) |  | Higher heating value (Btu/scf) |  | Moisture (%) |  |
| Specific gravity |  |  |  | Nitrogen (%) |  |
|  |  |  |  | Higher heating value (Btu/lb) |  |

### Field notes

| Document these observations | Notes |
| --- | --- |
| Exhaust measurement location; Existing heat-recovery equipment; Reading taken before or after existing recovery; Analyzer, load, photographs, and source notes. |  |

### Ready for MEASUR entry

|  | Baseline check |  | Baseline check |
| --- | --- | --- | --- |
| [ ] | Fuel, temperatures, oxygen or excess air, and fuel consumption are documented. | [ ] | The exhaust measurement location is clearly identified. |
| [ ] | Existing heat-recovery equipment and measurement position are recorded. | [ ] | No proposed recovered exhaust temperature is entered. |

# Compressed Air Systems

Use these records to document distribution velocity, inappropriate compressed-air uses, and individual leaks measured by the bag method.

## Opportunity 1 Check the velocity in compressed air piping

| MEASUR path: Compressed Air > Velocity in the Piping https://measur.ornl.gov/calculators/air-velocity | Scan to open |
| --- | --- |

Calculator context. Velocity in the Piping calculates air velocity for standard pipe sizes from airflow and pressure. Compare the output for the actual pipe size with the location-specific heuristic.

### Record identification

| Record field | Entry |
| --- | --- |
| System segment or line tag |  |
| Location or area |  |
| Assessment record number |  |

### Baseline inputs for Velocity in the Piping

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Location class | Compressor room, plant header, or final drop to an end use. |  |  |
| Airflow | Flow referenced to compressor inlet conditions. | scfm |  |
| Pipe pressure | Gauge pressure of air flowing through the segment. | psig |  |
| Atmospheric pressure | Site atmospheric pressure; 14.7 psia is a common sea-level value. | psia | 14.7 if applicable |
| Existing nominal pipe size | Use this field context to select the matching result in MEASUR. | in. |  |

### Velocity screening heuristics

| Location | Recommended maximum velocity |
| --- | --- |
| Compressed air room | No more than approximately 20 ft/s |
| Plant header | No more than approximately 30 ft/s |
| Final drop to an end use | No more than approximately 50 ft/s |

### Field notes

| Document these observations | Notes |
| --- | --- |
| Flow and pressure measurement sources; Pipe material, fittings, or restrictions; Noise or pressure-drop observations; Photographs and source notes. |  |

### Ready for MEASUR entry

|  | Baseline check |  | Baseline check |
| --- | --- | --- | --- |
| [ ] | Airflow, pressure, atmospheric pressure, and actual pipe size are documented. | [ ] | The segment location class is identified. |
| [ ] | Measurements represent the same current operating state. | [ ] | The MEASUR output will be compared with the correct location heuristic. |

## Opportunity 2 Reduce inappropriate compressed air use

| MEASUR path: Compressed Air > Compressed Air Reduction https://measur.ornl.gov/calculators/compressed-air-reduction | Scan to open |
| --- | --- |

Calculator context. Compressed Air Reduction quantifies current air consumption using a flow meter, bag test, orifice and pressure estimate, or another documented source. A calibrated flow-meter reading is preferred.

### Record identification

| Record field | Entry |
| --- | --- |
| Equipment or end-use tag |  |
| Area or process served |  |
| Assessment record number |  |

### Primary flow-meter baseline inputs

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Annual operating hours | Number of annual operating hours for the end use. | hrs/yr |  |
| Utility type | Select Purchased Compressed Air or Electricity. |  |  |
| Utility cost | Cost for the selected utility basis. | $/unit |  |
| Measurement method | Best available method for determining current compressed-air consumption. |  | Flow Meter |
| Flow-meter reading | Reading from a calibrated compressed-air flow meter. | scfm |  |
| Number of identical units | Number of identical end uses represented by the reading. | count |  |

### Optional measurement methods

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Bag volume | Bag Method input for the current end use. | gal |  |
| Bag fill time | Seconds required to fill the bag. | s |  |
| Nozzle type | Select the closest MEASUR nozzle or open-pipe type. |  |  |
| Number of nozzles | Count identical nozzles in the current end use. | count |  |
| Supply pressure | Pressure supplied at the point of use. | psig |  |
| Offsheet annual consumption | Use when consumption is available from another documented method. | kscf/yr |  |

### Electricity basis compressor inputs

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Electricity cost | Facility electricity cost per kilowatt-hour. | $/kWh |  |
| Trim compressor control | Control type of the compressor that responds to reduced demand. |  |  |
| Control adjustment | MEASUR default for the selected control or a documented custom value. | % |  |
| Compressor type | Reciprocating, lubricant-injected screw, lubricant-free screw, centrifugal, or custom. |  |  |
| Compressor specific power | Use measured or CAGI data when available. | kW/100 scfm |  |

### Field notes

| Document these observations | Notes |
| --- | --- |
| Reason the compressed air use may be inappropriate; Measurement method and location; Trim compressor and control source; Photographs and source notes. |  |

### Ready for MEASUR entry

|  | Baseline check |  | Baseline check |
| --- | --- | --- | --- |
| [ ] | Annual hours, utility basis, and utility cost are documented. | [ ] | The selected measurement method and its required inputs are complete. |
| [ ] | Identical-unit count is confirmed when applicable. | [ ] | Compressor control and specific power are available when using the electricity basis. |

## Opportunity 3 Quantify compressed air leaks using the bag method

| MEASUR path: Compressed Air > Leak Loss Estimator Bag Method https://measur.ornl.gov/calculators/bag-method | Scan to open |
| --- | --- |

Calculator context. The bag method estimates leak flow from the volume of a bag and the time required to fill it. Measure each leak separately, tag it, and record the system operating hours.

### Record identification

| Record field | Entry |
| --- | --- |
| Compressed air system |  |
| Area or route |  |
| Assessment record number |  |

### System baseline input

| Input | Field guidance | Unit | Baseline value or source |
| --- | --- | --- | --- |
| Annual system operating hours | Hours per year the compressed-air system is in use. | hrs/yr |  |

### Repeatable leak records

| Leak tag | Location | Bag volume gal | Fill time s | Photo or marker | Repair priority |
| --- | --- | --- | --- | --- | --- |

### Field notes

| Document these observations | Notes |
| --- | --- |
| Operating condition during leak tests; Bag dimensions or stated volume source; Leak access or safety constraints; Additional tagging and repair notes. |  |

### Ready for MEASUR entry

|  | Baseline check |  | Baseline check |
| --- | --- | --- | --- |
| [ ] | Annual system operating hours are documented. | [ ] | Each leak has a unique tag and location. |
| [ ] | Bag volume and fill time are recorded for every tested leak. | [ ] | No calculated flow, annual consumption, or savings result is entered in the field workbook. |